## Slide 1: IEEE-123 Bus Single Phase System

## Slide 2: Equivalent single phase 123-node system
voltage level for the system is 4.16 kV LL (2.4 kV LN)
transformer is removed by line with impedance (0.00001+j0.0001)
regulator is replaced by line segment with zero impedance
no capacitor in the system
To run base power flow following conditions are applied
all the load data is converted into star connected constant power load
no DG in the system
substation voltage at 1 pu (see IEEE123SinglePh.dss)
folder with the OpenDSS files‘IEEE123singlephase_baseOpenDSS’
Matlab calls OpenDSS using COM interface to solve powerflow
(see ‘IEEE123singlephase_basePowerflowvalidationOpenDSS_base.m’)

## Slide 3: IEEE-123 Node System
This is the base case model for the IEEE 123 bus single phase model
OpenDSS base model
Matlab base model

## Slide 4: Equivalent Matlab data
nodes are renumber to fit in the Matlab program
ex - node 150 == node 1
line capacitance is ignored
transformer is removed from the system
regulator is replaced by line segment with zero impedance
no capacitor in the system
To run base power flow following conditions are applied
all the load data is converted into star connected constant power load
no DG in the system
substation voltage at 1 pu
folder with the OpenDSS files ‘IEEE123singlephase_baseMatlab’

## Slide 5: Branch flow model
Active power
Reactive power
Voltage drop
Linear branch flow model
Current equation

## Slide 6: How to model in matlab?
Followings steps are followed for linear branch flow model:
impedance (R+jX) of the each line is obtained using openDSS (linedata.txt)
rated power of each node (P, Q) is obtained using openDSS (powerdata.txt)
taking ,
number of variables are defined
linear branch flow (LBF) equations are formulated as equality constraints (
for the power flow validation objective is
(see ‘singlephaselin.m’)

## Slide 7: Nonlinear branch flow (NLBF) equation
Following steps are required to model NLBF in Matlab:
impedance (R+jX) of the each line is obtained using openDSS (linedata.txt)
rated power of each node (P, Q) is obtained using openDSS (powerdata.txt)
taking ,
number of variables are defined
linear branch flow equations are formulated as equality constraints (
nonlinear branch flow equations are obtained (file ‘@eqcons’)
initial value obtained using LBF
for the power flow validation objective is
for solving the nonlinear programming problem ‘fmincon’ solver is called (see ‘nonlinpowerflow.m’)

## Slide 8: Power flow validation
OpenDSS |  | Matlab | 
Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
1201.5 | 716.71 | 1201.6 | 717.0
Base case power flow at substation
Voltage comparison between OpenDSS and Matlab

## Slide 9: IEEE 123 Bus feeder with 10% DG Penetration
DGs are placed randomly at 10% of load nodes
DGs rating at each node is equal to maximum rating of the load demand
DGs kVA rating is 120% of kW rating
Folder with OpenDSS and Matlab file ‘IEEE123singlephase_DG10’
OpenDSS model
Matlab model

## Slide 10: Power flow validation
OpenDSS |  | Matlab | 
Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
930.59 | 691.33 | 930.6 | 691.6
Voltage comparison between OpenDSS and Matlab
Power flow at substation with 10% DG penetration

## Slide 11: IEEE 123 Bus feeder with 30% Penetration
DGs are placed randomly at 30% of load nodes
DGs rating at each node is equal to maximum rating of the load demand
DGs kVA rating is 120% of kW rating
Folder with OpenDSS and Matlab file ‘IEEE123singlephase_DG30’
OpenDSS model
Matlab model

## Slide 12: Power flow validation
OpenDSS |  | Matlab | 
Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
737.63 | 678.51 | 737.6 | 678.8
Power flow at substation with 30% DG penetration
Voltage comparison between OpenDSS and Matlab

## Slide 13: IEEE 123 Bus feeder with 50% Penetration
DGs are placed randomly at 50% of load nodes
DGs rating at each node is equal to maximum rating of the load demand
DGs kVA rating is 120% of kW rating
Folder with OpenDSS and Matlab file ‘IEEE123singlephase_DG50’
OpenDSS model
Matlab model

## Slide 14: Power flow validation
OpenDSS |  | Matlab | 
Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
527.32 | 667.76 | 527.2 | 668.0
Power flow at substation with 50% DG penetration
Voltage comparison between OpenDSS and Matlab

## Slide 15: IEEE-123 Node System
This is the base case model for the IEEE 123 bus single phase model with 4 voltage regulator and 4 capacitor banks
The addition of PV at each node for 10%, 30% and 50% penetration is similar to previous slides

## Slide 16: Power flow validation base case
OpenDSS |  | Matlab | 
Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
1201.45 | 716.69 | 1201.6 | 717.1
Power flow at substation with four VR and four capacitor banks
Voltage comparison between OpenDSS and Matlab
Here all the capacitor banks switch are ON and supplying their rated Q
Tap positon of all the voltage regulators are 0

## Slide 17: Power flow validation base case
Matlab |  | OpenDSS | 
Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
1201.2 | 716.2 | 1201.05 | 715.9
Power flow at substation with four VR and four capacitor banks
Voltage comparison between OpenDSS and Matlab
Here all the capacitor banks switch are ON and supplying their rated Q
Tap positon of all the voltage regulators are 1,-5,4 and -4

## Slide 18: Power flow validation with 10% penetration
Matlab |  | OpenDSS | 
Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
924.8 | 429.8 | 924.8 | 429.5
Power flow at substation with four VR and four capacitor banks
Voltage comparison between OpenDSS and Matlab
Here all the capacitor banks switch are ON and supplying their rated Q
Tap positon of all the voltage regulators are 0

## Slide 19: Power flow validation with 10% penetration
Matlab |  | OpenDSS | 
Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
924.6 | 429.4 | 924.8 | 429.2
Power flow at substation with four VR and four capacitor banks
Voltage comparison between OpenDSS and Matlab
Here all the capacitor banks switch are ON and supplying their rated Q
Tap positon of all the voltage regulators are 1,-5,4,-4

## Slide 20: Power flow validation with 30% penetration
Matlab |  | OpenDSS | 
Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
732.0 | 417.4 | 732.06 | 417.12
Power flow at substation with four VR and four capacitor banks
Voltage comparison between OpenDSS and Matlab
Here all the capacitor banks switch are ON and supplying their rated Q
Tap positon of all the voltage regulators are 0

## Slide 21: Power flow validation with 30% penetration
Matlab |  | OpenDSS | 
Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
731.9 | 417.2 | 732.26 | 417.07
Power flow at substation with four VR and four capacitor banks
Voltage comparison between OpenDSS and Matlab
Here all the capacitor banks switch are ON and supplying their rated Q
Tap positon of all the voltage regulators are 1,-5,4,-4

## Slide 22: Power flow validation with 50% penetration
Matlab |  | OpenDSS | 
Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
521.9 | 407.0 | 521.89 | 406.71
Power flow at substation with four VR and four capacitor banks
Voltage comparison between OpenDSS and Matlab
Here all the capacitor banks switch are ON and supplying their rated Q
Tap positon of all the voltage regulators are 0

## Slide 23: Power flow validation with 50% penetration
Matlab |  | OpenDSS | 
Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
521.8 | 406.9 | 521.83 | 406.59
Power flow at substation with four VR and four capacitor banks
Voltage comparison between OpenDSS and Matlab
Here all the capacitor banks switch are ON and supplying their rated Q
Tap positon of all the voltage regulators are 1,-5,4,-4

## Slide 24: Power flow validation with Capacitor and 1 Voltage Regulator
Base case power flow at substation
Legacy Device | OpenDSS |  | Matlab | 
Status | Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
C sw = 1, VR tap=0 | 1195.3 | 454.2 | 1195.3 | 454.03
C sw = 1, VR tap=1 | 1194.9 | 453.5 | 1194.9 | 453.14
C sw = 1, VR tap=-5 | 1197.7 | 459.0 | 1197.6 | 458.65
Legacy Device | OpenDSS |  | Matlab | 
Status | Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
C sw = 1, VR tap=0 | 924.8 | 429.8 | 924.83 | 429.51
C sw = 1, VR tap=-1 | 925.1 | 430.4 | 925.07 | 430.04
C sw = 1, VR tap=5 | 923.6 | 427.3 | 923.55 | 426.93
Power flow at substation with 10% DG penetration

## Slide 25: Power flow validation with Capacitor and 1 Voltage Regulator
Legacy Device | OpenDSS |  | Matlab | 
Status | Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
C sw = 1, VR tap=0 | 732.0 | 417.4 | 732.07 | 417.13
C sw = 1, VR tap=1 | 731.9 | 417.1 | 731.79 | 416.69
C sw = 1, VR tap=-5 | 733.0 | 419.4 | 733.01 | 419.06
Legacy Device | OpenDSS |  | Matlab | 
Status | Active Power (kW) | Reactive Power (kVAr) | Active Power (kW) | Reactive Power (kVAr)
C sw = 1, VR tap=0 | 521.9 | 407.0 | 521.89 | 406.71
C sw = 1, VR tap=1 | 521.8 | 406.8 | 521.84 | 406.51
C sw = 1, VR tap=-5 | 522.5 | 408.3 | 522.54 | 407.95
Power flow at substation with 50% DG penetration
Power flow at substation with 30% DG penetration